60Hz R410A DC INVERTER SERIES

Service Manual 2017

Part 1 General Information	1

Part 2 Indoor Units	5

Part 3 Outdoor Units	63

Part 4 Installation	72

Part 5 Electrical Control System	105

※The specifications, designs, and information in this book are subject to change without notice for product improvement.

Part 1
General Information

1. Model Names of Indoor/Outdoor Units	2

2. External Appearance	3

2.1 Indoor Units	3

2.2 Outdoor Units	3

3. Nomenclature	4

Model lists

1.1 Indoor Units

| R410A | Capacity multiplied by 1000Btu/h |
| --- | --- |
| Type | Function | 24 | 36 | 48 | 55 |
| Ceiling & Floor | Cooling only | ● | ● | ● | ● |
| Super slim cassette | Cooling only | ● | ● | ● | ● |
| Duct | Cooling only | ● | ● | ● | ● |
| Air Handler | Cooling only | ● |  |  |  |

1.2 Outdoor Units

| Universal Outdoor unit Model | Compressor type | Compressor Brand | Matched indoor units |
| --- | --- | --- | --- |
| Heat Pump |
| MOV-24CDN1-N | Rotary | GMCC | MUE-24CRDN1-N(B) MCD-24CRDN1-N MTI-24CWDN1-N MVB-24CWDN1-N |
| MOV-36CDN1-N | Rotary | GMCC | MUE-36CRDN1-N MCD-36CRDN1-N MTB-36CWDN1-N |
| MOV-48CDN1-N | Rotary | GMCC | MUE-48CRDN1-N(B) MCD-48CRDN1-N(B) MTB-48CWDN1-N |
| MOV-55CDN1-N | Rotary | GMCC | MUE-55CRDN1-N MCD-55CRDN1-N MTB-55CWDN1-N |

External Appearance

2.1 Indoor Units

| Super slim cassette | Duct |
| --- | --- |
| Ceiling-Floor | Air Handler |

2.2 Outdoor Units

Nomenclature

  - Indoor Unit

3.2 Outdoor Unit

Part 2
Indoor Units

Ceiling & Floor Type	6

Super Slim Cassette Type	15

A5 Duct Type	27

A6 Duct Type	40

Air Handler Indoor Unit Type	53

Ceiling & Floor Type

1. Features	7

2. Dimensions	8

3. Service Space	9

4. Wiring Diagrams	10

5. Electric Characteristics	11

6. Sound Levels	11

7. Accessories	12

8. The Specification of Power	13

9. Field Wiring	14

Features

  - New design, more modern and elegant appearance.

1.2.	Convenient installation

--The ceiling type can be easily installed into a corner of the ceiling even if the ceiling is very narrow

--It is especially useful when installation of an air conditioner in the center of the ceiling is impossible due to a structure such as one lighting.

1.3.	Two direction auto swing (vertical & horizontal) and wide angle air flow,

--Air flow directional control minimizes the air resistance and produces wilder air flow to vertical direction.

--The range of horizontal air discharge is widened which secures wider air flow distribution to provide more comfortable air circulation no matter where the unit is set up

1.4.	Three level fan speed, more humanism design, meets different air-supply requirement.

1.5.	New foam drain pan with plastic-spraying inner surface

1.6.	Easy operation.

1.7.	Remote control and optional wired control method.

Dimensions

| Capacity (Btu/h) | A | B | C | D |
| --- | --- | --- | --- | --- |
| 24K | 1068 | 675 | 235 | 983 |
| 36K | 1285 | 675 | 235 | 1200 |
| 45K | 1650 | 675 | 235 | 1565 |
| 55K | 1650 | 675 | 235 | 1565 |

Service Space

Wiring Diagrams

MUE-24CRDN1-N(B)

MUE-36CRDN1-N MUE-48CRDN1-N(B) MUE-55CRDN1-N

Electric Characteristics

| Model | Indoor Units | Power Supply |
| --- | --- | --- |
|  | Hz | Voltage | Min. | Max. | MFA |
| MUE-24CRDN1-N(B) | 60 | 220-230V | 198V | 242V | / |
| MUE-36CRDN1-N | 60 | 220-230V | 198V | 242V | / |
| MUE-48CRDN1-N(B) | 60 | 220-230V | 198V | 242V | / |
| MUE-55CRDN1-N | 60 | 220-230V | 198V | 242V | / |

Note:

MFA: Max. Fuse Amps. (A)

Sound Levels

Ceiling	Floor

| Model | Noise level dB(A) |
| --- | --- |
|  | H | M | L |
| MUE-24CRDN1-N(B) | 52 | 45 | 38 |
| MUE-36CRDN1-N | 54 | 52 | 46 |
| MUE-48CRDN1-N(B) | 59 | 56 | 53 |
| MUE-55CRDN1-N | 59 | 56 | 54 |

Accessories

| Remote controller & Its holder | 1. Remote controller |  | 1 |
| --- | --- | --- | --- |
|  | 2. Remote controller holder(optional) |  | 1 |
|  | 3. Mounting screw (ST2.9×10-C-H) |  | 2 |
|  | 4. Alkaline dry batteries (AM4) |  | 2 |
| Others | 5. Owner's manual |  | 1 |
|  | 6. Installation manual |  | 1 |
|  | 7. Remote controller manual |  | 1 |

The Specification of Power

| Type | 24000 | 36000 | 48000 | 55000 |
| --- | --- | --- | --- | --- |
| Indoor Unit Power | Phase |  |  |  |  |
|  | Frequency and Voltage |  |  |  |  |
|  | Power Wiring (mm2) |  |  |  |  |
|  | Circuit Breaker/ Fuse (A) |  |  |  |  |
| Outdoor Unit Power | Phase | 1- Phase | 1- Phase | 1- Phase | 1- Phase |
|  | Frequency and Voltage | 220-230V~, 60Hz | 220-230V~, 60Hz | 220-230V~, 60Hz | 220-230V~, 60Hz |
|  | Power Wiring (mm2) | 3×2.5 | 3×4.0 | 3×6.0 | 3×6.0 |
|  | Circuit Breaker/ Fuse (A) | 30/20 | 40/30 | 40/35 | 50/40 |
| Indoor/Outdoor Connecting Wiring (mm2) | Weak Electric Signal (mm2) |  |  |  |  |
|  | Strong Electric Signal (mm2) | 4×1.0 | 4×1.0 | 4×1.0 | 4×1.0 |

Field Wiring

Super Slim Cassette Type

1. Features	16

2. Dimensions	19

3. Service Space	20

4. Wiring diagrams	21

5. Electric Characteristics	22

6. Sound Levels	23

7. Accessories	24

8. The Specification of Power	25

9. Field Wiring	26

Features

  - Overview

- Compact design, super slim body size, less space requiring in installation

- Each louver can be separately controlled, more comfort air blowing is possible.

- Auto-lifting panel design, more convenient to clean and maintain the filter. (optional)

  - Fresh air intake function

- Fresh air fulfills air quality more healthy and comfortable.

- Ventilation motor is optional to increase the effect of fresh air.

  - Optional ionizer generator

- Ionizer generator is optional to get refreshing air to your room.

Ionizer generator

connector

Ventilation motor connector

- Ionizer can be switched on or off by remote controller.

When pressing the Clean Air button on the remote controller, Ionizer will work and the indicator light on display board will shine.

  - External air duct design

- Reserve external  air duct, more flexible for the air supply.

  - Built-in draining pump

- Due to the improvement of structure, more convenient to repair or replace the draining pump.

Draining Pump

- Built-in draining pump to make sure condensed water drain out reliably.

  - Terminals for alarm lamp and long-distance on-off controller connection are standard

- Reserve terminals for the connection of alarm lamp and long-distance on-off controller, more human control.

Alarm lamp

Long-distance on-off controller

  - Twins Combination(18k-30k)

- The units can be installed as Twin systems: one outdoor unit can connect with two indoor units. The indoor units can be combined in any of the different available ratings.

Dimensions

| Unit: mm |
| --- |
| Capacity (KBtu/h) | A | B | C | D |
| 24 | 160 | 75 | 205 | 50 |
| 36/48/55 | 160 | 95 | 287 | 60 |

Service Space

Wiring diagrams

MCD-24CRDN1-N

MCD-36CRDN1-N MCD-48CRDN1-N(B) MCD-55CRDN1-N

Electric Characteristics

| Model | Indoor Unit | Power Supply |
| --- | --- | --- |
|  | Hz | Voltage | Min | Max | MFA |
| MCD-24CRDN1-N | 60 | 220-230 | 198 | 242 | / |
| MCD-36CRDN1-N | 60 | 220-230 | 198 | 242 | / |
| MCD-48CRDN1-N(B) | 60 | 220-230 | 198 | 242 | / |
| MCD-55CRDN1-N | 60 | 220-230 | 198 | 242 | / |

Notes:

MFA: Max. Fuse Amps. (A)

Sound Levels

| Model | Noise level dB(A) |
| --- | --- |
|  | H | M | L |
| MCD-24CRDN1-N | 43 | 39 | 33 |
| MCD-36CRDN1-N | 52 | 46 | 41 |
| MCD-48CRDN1-N(B) | 51 | 44 | 42 |
| MCD-55CRDN1-N | 53 | 45 | 43 |

Accessories

|  | Name | Shape | Quantity |
| --- | --- | --- | --- |
| Installation Fittings | Installation paper board |  | 1 |
| Tubing & Fittings | Soundproof / insulation sheath |  | 1 |
| Drainpipe Fittings | Out-let pipe sheath |  | 1 |
|  | Out-let pipe clasp |  | 1 |
|  | Drain joint |  | 1 |
|  | Seal ring |  | 1 |
| Remote controller & Its Frame(The product you have might not be provided the following accessories) | Remote controller & Its Frame |  | 1 |
|  | Remote controller holder |  | 1 |
|  | Mounting screw(ST2.9×10-C-H) |  | 2 |
|  | Remote controller manual |  | 1 |
|  | Alkaline dry batteries (AM4) |  | 2 |
| Others | Owner's manual |  | 1 |
|  | Installation manual |  | 1 |
| Installation accessory (The product you have might not be provided the following accessories | Expansible hook |  | 4 |
|  | Installation hook |  | 4 |
|  | Orifice |  | 1 |
| EMC Magnetic Ring (some models) | Magnetic ring (wrap the electric wires P & Q & E around the magnetic ring twice) |  | 1 |

The Specification of Power

| ype | 24000 | 36000 | 48000 | 55000 |
| --- | --- | --- | --- | --- |
| Indoor Unit Power | Phase |  |  |  |  |
|  | Frequency and Voltage |  |  |  |  |
|  | Power Wiring (mm2) |  |  |  |  |
|  | Circuit Breaker/ Fuse (A) |  |  |  |  |
| Outdoor Unit Power | Phase | 1- Phase | 1- Phase | 1- Phase | 1- Phase |
|  | Frequency and Voltage | 220-230V~, 60Hz | 220-230V~, 60Hz | 220-230V~, 60Hz | 220-230V~, 60Hz |
|  | Power Wiring (mm2) | 3×2.5 | 3×4.0 | 3×6.0 | 3×6.0 |
|  | Circuit Breaker/ Fuse (A) | 25/20 | 40/30 | 50/40 | 50/40 |
| Indoor/Outdoor Connecting Wiring (mm2) | Weak Electric Signal (mm2) |  |  |  |  |
|  | Strong Electric Signal (mm2) | 4×1.0 | 4×1.0 | 4×1.0 | 4×1.0 |

Field Wiring

A5 Duct Type

1. Features	28

2. Dimensions	31

3. Service Space	32

4. Wiring Diagrams	33

5. Static Pressure	34

6. Electric Characteristics	35

7. Sound Levels	36

8. Accessories	37

9. The Specification of Power	38

10. Field Wiring	39

Features

1.1 Installation accessories: (Optional)

- Front Board, Canvas Air Passage, Filter, Panel, for easy installation

Front Board

Filter

Panel

1.2 Easy Installation: Two air inlet styles (Bottom side or Rear side)

- Air inlet from rear is standard for all capacity; air inlet from bottom is optional.

- The size of air inlet frame from rear and bottom is same, it’s very easy to move the cover from bottom to rear side, or from rear to the bottom, in order to matching the installation condition.

Air intake from bottom (Optional)

Air intake from rear (Standard)

1.3 Fresh air intake function(Optional for 18~60k)

- Install one duct from the reserved fresh-air intake to outdoor.

Continually inhale the fresh air to improve the quality of the indoor air, fulfills air quality more healthy and comfortable.

1.4 Easy maintenance

- Clean the filter (Optional, standard product without filter)

It is easy to draw out the filter from the indoor unit for cleaning, even the filter is installed in rear side or bottom side.

- Replace the motor or centrifugal fan

Remove the ventilated panel firstly. Remove a half of blower housing and take out the motor with centrifugal fan. Directly remove two bolts, and then replace the motor or centrifugal fan easily.

Ventilated Panel

Blower Housing

Motor

1.5 Reserved remote on-off and central control ports

- Reserved remote on-off ports and central control ports, can connect the cable of an on-off controller or a central controller to realize remote on-off control function or group control function.

Central control ports

Remote on-off ports

1.6 Built-in drain pump (Optional):

- Built-in drain pump can lift the water to 750mm upmost. It’s convenient to install drainage piping under most space condition.

750mm upmost

1.7 Built-in display board

- The standard indoor unit can be controlled by wired controller.

- There is a display board with a receiver in the E-box. Move out the display, and fix it in other place, even in the distance of 2m. The unit will realized remoter control.

- The wired controller and the display board can display the error code or production code when the chips detect some failure.

Wired Controller (Standard)

Remote Controller (Optional)

Display

Dimensions

| Note: standard product without filter Unit: mm |
| --- |
| Capacity (KBtu/h) | Outline dimension(mm) | Air outlet opening size | Air return opening size | Size of install hanger | Size of refrigerant pipe |
|  | A | B | C | D | E | F | G | H | I | J | K | L | M | H1 | H2 | W1 | W2 |
| 36/48/55 | 1200 | 300 | 865 | 800 | 80 | 968 | 40 | 204 | 1094 | 288 | 45 | 1240 | 500 | 175 | 198 | 155 | 210 |

Service Space

Ensure enough space required for installation and maintenance.

All the indoor units reserve the hole to joint the fresh air pipe. The hole size as following:

Wiring Diagrams

MTB-48CWDN1-N

MTB-36CWDN1-N  MTB-55CWDN1-N

Static Pressure

Electric Characteristics

| Model | Indoor Unit | Power Supply |
| --- | --- | --- |
|  | Hz | Voltage | Min | Max | MFA |
| MTB-36CWDN1-N | 60 | 220-230 | 198 | 242 | / |
| MTB-48CWDN1-N | 60 | 220-230 | 198 | 242 | / |
| MTB-55CWDN1-N | 60 | 220-230 | 198 | 242 | / |

Notes:

MFA: Max. Fuse Amps. (A)

Sound Levels

| Model | Noise level dB(A) |
| --- | --- |
|  | H | M | L |
| MTB-36CWDN1-N | 48 | 43 | 39 |
| MTB-48CWDN1-N | 47 | 43 | 41 |
| MTB-55CWDN1-N | 47 | 43 | 39 |

Accessories

|  | Name | Shape | Quantity |
| --- | --- | --- | --- |
| Tubing & Fittings | Soundproof / insulation sheath |  | 2 |
|  | Binding tape(some models) |  | 1 |
|  | Seal sponge(some models) |  | 1 |
| Drainpipe Fittings (for cooling & heating) | Drain joint(some models) |  | 1 |
|  | Seal ring(some models) |  | 1 |
| Wired controller & Its Frame | Wired controller |  | 1 |
| Others | Owner，s manual |  | 1 |
|  | Installation manual |  | 1 |
| EMS & It’s fitting | Magnetic ring (twist the electric wires L and N around it to five circles) |  | 1 |

The Specification of Power

| Type | 36000 | 48000 | 55000 |
| --- | --- | --- | --- |
| Indoor Unit Power | Phase |  |  |  |
|  | Frequency and Voltage |  |  |  |
|  | Power Wiring (mm2) |  |  |  |
|  | Circuit Breaker/ Fuse (A) |  |  |  |
| Outdoor Unit Power | Phase | 1- Phase | 1- Phase | 1- Phase |
|  | Frequency and Voltage | 220-230V~, 60Hz | 220-230V~, 60Hz | 220-230V~, 60Hz |
|  | Power Wiring (mm2) | 3×4.0 | 3×6.0 | 3×6.0 |
|  | Circuit Breaker/ Fuse (A) | 40/30 | 50/40 | 50/40 |
| Indoor/Outdoor Connecting Wiring (mm2) | Weak Electric Signal (mm2) |  |  |  |
|  | Strong Electric Signal (mm2) | 4×1.0 | 4×1.0 | 4×1.0 |

Field Wiring

A6 Duct Type

1. Features	41

2. Dimensions	45

3. Service Space	46

4. Wiring Diagrams	47

5. Static Pressure	48

6. Electric Characteristics	48

7. Sound Levels	49

8. Accessories	50

9. The Specification of Power	51

10. Field Wiring	52

- Features

1.1 Higher Static Pressure

- As a ducted air conditioner with medium static pressure, it has the widest static pressure range.

- The maximum static pressure reaches 160 Pa

  - Slim Design

- The industry Lowest height is designed to be fitted into tight roof spaces.

*18K unit - 210mm,24K/36K unit - 249mm，48K unit -300mm

  - Constant air volume control

- For ordinary duct, when the static pressure exceeds the expected range, it is fairly difficult even for an experienced installer to calculate and adjust the air volume precisely.

- With constant air volume control technology, the duct will automatically adjusts to perfect static pressure and keep constant air volume.

1.4 Installation accessories: (Optional)

- Front Board, Canvas Air Passage, Filter, Panel, for easy installation

Front Board

Filter

Panel

1.5 Flexible Air Intake Way (Bottom side or Rear side)

- The frame size of air inlet in rear and bottom is the same. It’s very easy to switch to match different application.

Air intake from bottom (Optional)

Air intake from rear (Standard)

1.6 Communication wire connection

- A6 duct uses two wires without polarity connection way, which almost has no mistake during the installation.

1.7 Easy Clean

- Clean the filter (Optional, standard product without filter)

- It is easy to draw out the filter from the indoor unit for cleaning, even the filter is installed in rear side or bottom side.

- With a larger window design, once the  motor and the blower wheels have been detached,  heat exchanger and water receiver tray in behind can be seen very clearly. Dust can be easily removed from the inside by vacuum

1.8 Easy maintenance

- A6 duct allows operators maintenance the motor from the bottom more easily compare with that on the top.

- A6 duct has big space for maintenance at the side

1.9 Fresh air intake function(Optional)

- Install one duct from the reserved fresh-air intake to outdoor.

Continually inhale the fresh air to improve the quality of the indoor air, fulfills air quality more healthy and comfortable.

- A  ventilation motor (provided by the installer) can be installed inside the fresh air duct to improve the fresh air volume. There are reserved ports for this motor on main PCB (Standard for 3D inverter units, and  only optional for DC inverter 53~160 units).

1.10 Built-in drain pump (Optional)

- Built-in drain pump can lift the water to 750mm upmost, which widens the drainage piping range.

Max 750mm

Dimensions

| Note: standard product without filter Unit: mm |
| --- |
| Capacity (KBtu/h) | Outline dimension(mm) | Air outlet opening size | Air return opening size | Size of install hanger | Size of refrigerant pipe |
|  | A | B | C | D | E | F | G | H | I | J | K | L | M | H1 | H2 | W1 | W2 |
| 24 | 1100 | 249 | 774 | 700 | 140 | 926 | 50 | 175 | 1001 | 228 | 5 | 1140 | 598 | 80 | 150 | 130 | 155 |

Service Space

Ensure enough space required for installation and maintenance.

All the indoor units reserve the hole to joint the fresh air pipe. The hole size as following:

Wiring Diagrams

MTI-24CWDN1-N

Static Pressure

24k

Electric Characteristics

| Model | Indoor Unit | Power Supply |
| --- | --- | --- |
|  | Hz | Voltage | Min | Max | MFA |
| MTI-24CWDN1-N | 60 | 220-230 | 198 | 242 | / |

Notes:

MFA: Max. Fuse Amps. (A)

Sound Levels

| Model | Noise level dB(A) |
| --- | --- |
|  | H | M | L |
| MTI-24CWDN1-N | 42 | 38 | 32 |

Accessories

|  | Name | Shape | Quantity |
| --- | --- | --- | --- |
| Tubing & Fittings | Soundproof / insulation sheath |  | 2 |
|  | Seal sponge(some models) |  | 1 |
|  | Orifice (some models) |  | 1 |
| Drainpipe Fittings (for cooling & heating) | Drain joint(some models) |  | 1 |
|  | Seal ring(some models) |  | 1 |
| Wired controller & Its Frame | Wired controller |  | 1 |
| Others | Owner，s manual |  | 1 |
|  | Installation manual |  | 1 |
| EMC Magnetic Ring (some models) | Magnetic ring (wrap the electric wires S1 & S2 ( P & Q & E ) around the magnetic ring twice) |  | 1 |
|  | Magnetic ring (Hitch on the connective cable between the indoor unit and outdoor unit after installation.) |  | 1 |

The Specification of Power

| Type | 24000 |
| --- | --- |
| Indoor Unit Power | Phase |  |
|  | Frequency and Voltage |  |
|  | Power Wiring (mm2) |  |
|  | Circuit Breaker/ Fuse (A) |  |
| Outdoor Unit Power | Phase | 1- Phase |
|  | Frequency and Voltage | 220-230V~, 60Hz |
|  | Power Wiring (mm2) | 3×2.5 |
|  | Circuit Breaker/ Fuse (A) | 25/20 |
| Indoor/Outdoor Connecting Wiring (mm2) | Weak Electric Signal (mm2) |  |
|  | Strong Electric Signal (mm2) | 4×1.0 |

Field Wiring

Air Handler Type

1. Features	54

2. Dimensions	55

3. Service Space	56

4. Wiring Diagrams	57

5. Static Pressure	58

6. Electric Characteristics	59

7. Sound Levels	60

9. The Specification of Power	61

10. Field Wiring	62

- Features

1.1 Cabinet

- The enclosure is built with galvanized steel and coated with a protective paint. It is convenient for transportation and installation and fully insulated from high temperature and high voltage, in order to avoid hazardous risks.

1.2 Filter

- Factory installed filter can be cleaned and reinstalled for air filtration.

Air Filter

Seal Beam

1.3 Drainage

- Enhancing primary and second drainage design allows complete drainage to improve in-house air quality.

1.4 Protection

- Factory installed coil temperature sensor providing effective protection of the system.

1.5 Expansion Device

- The Valve Expansion Device is durable and guarantees stable operation.

1.6 Application

- Multiple airflow positions design, which includes up-flow, horizontal, enables an extensive share of the air exchanged.

1.7 Performance

This series is designed and tested by ARI 210/240 standard.

Dimensions

|  | Unit: inch (mm) |
| --- | --- |
| Capacity (Btu/h) | A | B | C | D | E |
| 24K | 30-1/2 (774) | 20-1/2 (520) | 18-1/8 (460) | 16-1/4 (414) | 9-5/8 (245) |

Service Space

- Refrigerant piping and connections- minimum12" recommended.

- Maintenance and servicing access - minimum36" from front of unit recommended for blower motor/coil replacement.

- Filter removal - minimum 36" recommended.

- Plenum Clearances:

Wiring Diagrams

MVB-24CWDN1-N

Static Pressure

Electric Characteristics

| Model | Indoor Units | Power Supply |
| --- | --- | --- |
|  | Hz | Voltage | Min. | Max. | MFA |
| MVB-24CWDN1-N | 60 | 220-230V | 198V | 242V | / |

Note:

MFA: Max. Fuse Amps. (A)

Sound Levels

| Model | Noise level dB(A) |
| --- | --- |
|  | H | L |
| MVB-24CWDN1-N | 48 | 45 |

8．Accessories

| Name | Shape | Quantity |
| --- | --- | --- |
| Pass line rubber ring |  | 2 |
| Owner’s and Installation manual |  | 1 |
| Display panel *Just for testing purposes only |  | 1(on some models) |

- The Specification of Power

| Capacity(Btu/h) | 24K |
| --- | --- |
| Power | Phase | 1PH |
|  | Frequency/Voltage | 220-230V, 60Hz |
| Input Current Fuse | Indoor unit(A) | 5A |
| Lines Gauge | Indoor Unit Power Line | Line Quantity | 3 |
|  |  | Line Diameter(AWG) | 18/1.0mm2 |
|  | Outdoor Unit Power Line | Line Quantity | 3 |
|  |  | Line Diameter(AWG) | 14/2.5mm2 |
|  | Outdoor-Indoor Signal Line | Lines Quantity | 2 |
|  |  | Line Diameter(AWG) | 18/1.0mm2 |
|  | Thermostat Signal Line | Lines Quantity | 4 |
|  |  | Line Diameter(AWG) | 18/1.0mm2 |

Field Wiring

Part 3 
Outdoor Units

1.	Dimensions	64

2.	Service Space	65

3.	Piping Diagrams	66

4.	Wiring Diagrams	67

5.	Electric Characteristics	70

6.	Operation Limits	70

7. Sound Levels	71

- Dimensions

| Unit Model (Btu/h) | Dimensions (Inches) | Refrigerant Connection Service Valve Size |
| --- | --- | --- |
|  | "H" in [mm] | "W" in [mm] | "L" in [mm] | Liquid in | Vapor in |
| MOV-24CDN1-N | 24-15/16[633] | 23-5/8[600] | 23-5/8[600] | 3/8 | 5/8 |
| MOV-36CDN1-N | 33-3/16[843] | 28[710] | 28[710] | 3/8 | 5/8 |
| MOV-48CDN1-N | 33-3/16[843] | 28[710] | 28[710] | 3/8 | 7/8 |
| MOV-55CDN1-N | 33-3/16[843] | 28[710] | 28[710] | 3/8 | 7/8 |

- Service Space

- Piping Diagrams

MOV-24CDN1-N

MOV-36CDN1-N  MOV-48CDN1-N  MOV-55CDN1-N

- Wiring Diagrams

MOV-24CDN1-N

MOV-36CDN1-N

MOV-48CDN1-N  MOV-55CDN1-N

- Electric Characteristics

| Model | Power Supply |
| --- | --- |
|  | Hz | Phase | Voltage | Min. | Max. | MFA |
| MOV-24CDN1-N | 60 | 1 | 220-230V | 198V | 242V | 20 |
| MOV-36CDN1-N | 60 | 1 | 220-230V | 198V | 242V | 30 |
| MOV-48CDN1-N | 60 | 1 | 220-230V | 198V | 242V | 40 |
| MOV-55CDN1-N | 60 | 1 | 220-230V | 198V | 242V | 40 |

Notes:

MFA: Max. Fuse Amps. (A)

- Operation Limits

| Temperature Mode | Cooling operation |
| --- | --- |
| Room temperature | 17℃～32℃ |
| Outdoor temperature | 0℃～50℃ |
|  | （-15℃～50℃：For the models with low temperature cooling system） |

- Sound Levels

| Model | Noise level dB(A) |
| --- | --- |
| MOV-24CDN1-N | 60 |
| MOV-36CDN1-N | 66 |
| MOV-48CDN1-N | 63 |
| MOV-60CDN1-N | 67 |

Part 4
Installation

1.	Installation Procedure	73

2.	Location selection	74

3.	Indoor unit installation	75

4.	Outdoor unit installation (Top Discharge Unit)	91

5.	Refrigerant pipe installation	94

6.	Drainage pipe installation	96

7.	Vacuum Drying and Leakage Checking	100

8.	Additional refrigerant charge	101

9.	Engineering of insulation	102

10.Engineering of electrical wiring	103

11.	Test operation	104

Installation Procedure

Vacuum drying and leakage checking

Additional refrigerant charge

Insulation the joint part of refrigerant pipe

Wiring connection and electric safety checking

Test operation

Refrigerant pipe installation and insulation

Drainage pipe installation and insulation

Indoor unit installation location selection

Outdoor unit installation location selection

Indoor unit installation

Outdoor unit installation

Refrigerant pipe installation and insulation

Drainage pipe installation and insulation

Location selection

- Indoor unit location selection

- The place shall easily support the indoor unit’s weight.

- The place can ensure the indoor unit installation and inspection.

- The place can ensure the indoor unit horizontally installed.

- The place shall allow easy water drainage.

- The place shall easily connect with the outdoor unit.

- The place where air circulation in the room should be good.

- There should not be any heat source or steam near the unit.

- There should not be any oil gas near the unit

- There should not be any corrosive gas near the unit

- There should not be any salty air neat the unit

- There should not be strong electromagnetic wave near the unit

- There should not be inflammable materials or gas near the unit

- There should not be strong voltage vibration.

- Outdoor unit location selection

- The place shall easily support the outdoor unit’s weight.

- Locate the outdoor unit as close to indoor unit as possible

- The piping length and height drop can not exceed the allowable value.

- The place where the noise, vibration and outlet air do not disturb the neighbors.

- There is enough room for installation and maintenance.

- The air outlet and the air inlet are not impeded, and not face the strong wind.

- It is easy to install the connecting pipes and cables.

- There is no danger of fire due to leakage of inflammable gas.

- It should be a dry and well ventilation place

- The support should be flat and horizontal

- Do not install the outdoor unit in a dirty or severely polluted place, so as to avoid blockage of the heat exchanger in the outdoor unit.

- If is built over the unit to prevent direct sunlight, rain exposure, direct strong wend, snow and other scraps accumulation, make sure that heat radiation from the condenser is not restricted.

Indoor unit installation

- Ceiling & floor indoor unit installation

- Service space for indoor unit

- Bolt pitch

① Ceiling installation

| Capacity (Btu/h) | D | E |
| --- | --- | --- |
| 24K | 983 | 220 |
| 36K | 1200 | 220 |
| 48K, 55K | 1565 | 220 |

② Wall-mounted installation

- Install the pendant bolt

① Ceiling installation

Select the position of installation hooks according to the hook holes positions showed in upper picture.

Drill four holes of Ø12mm, 45~50mm deep at the selected positions on the ceiling. Then embed the expansible hooks (fittings).

② Wall-mounted installation

Install the tapping screws onto the wall.(Refer to picture below)

- Install the main body

① Ceiling installation (The only installation method for the unit with drain pump)

Remove the side board and the grille.

Locate the hanging arm on the hanging screw bolt. Prepare the mounting bolts on the unit.

Put the side panels and grilles back.

② Wall-mounted installation

Hang the indoor unit by insert the tapping screws into the hanging arms on the main unit. (The bottom of body can touch with floor or suspended, but the body must install vertically.)

- Super slim cassette indoor unit installation

- Service space for indoor unit

| Capacity(KBtu) | A | H |
| --- | --- | --- |
| 24 | 205 | > 235 |
| 36/48/55 | 287 | >317 |

- Bolt pitch

- Install the pendant bolt

Select the position of installation hooks according to the hook holes positions showed in upper picture.

Drill four holes of Ø12mm, 45~50mm deep at the selected positions on the ceiling. Then embed the expansible hooks (fittings).

- Install the main body

Make the 4 suspender through the 4 hanger of the main body to suspend it. Adjust the hexangular nuts on the four installation hooks evenly, to ensure the balance of the body. Use a leveling instrument to make sure the levelness of the main body is within ±1°.

Adjust the position to ensure the gaps between the body and the four sides of ceiling are even. The body's lower part should sink into the ceiling for 10~12 mm. In general, L is half of the screw length of the installation hook.

Locate the air conditioner firmly by wrenching the nuts after having adjusted the body's position well.

- Install the panel

Remove the grille

Remove the 4 corner covers.

Hang the panel to the hooks on the mainbody. If the panel is with auto-lift grille, please watch the ropes lifing the grille, DO NOT make the ropes enwinded or blocked.

Tighten the screws under the panel hooks till the panel closely stick on the ceiling to avoid condensate water.

Hang the air-in grill to the panel, then connect the lead terminator of the swing motor and that of the control box with corresponding terminators on the body respectively.

Install the 4 corner covers back.

Note: The panel shall be installed after the wiring connected.

- A5 Duct indoor unit installation

- Service space for indoor unit

- Bolt pitch

| Capacity(KBtu) | Size of outline dimension mounted plug |
| --- | --- |
|  | L | M |
| 36/48/55 | 1240 | 500 |

- Install the pendant bolt

Select the position of installation hooks according to the hook holes positions showed in upper picture.

Drill four holes of Ø12mm, 45~50mm deep at the selected positions on the ceiling. Then embed the expansible hooks (fittings).

- Install the main body

Make the 4 suspender through the 4 hanger of the main body to suspend it. Adjust the hexangular nuts on the four installation hooks evenly, to ensure the balance of the body. Use a leveling instrument to make sure the levelness of the main body is within ±1°.

- Install the air filter

Insert the air filter through the filter slot and fix it with 2 screws.

- Install the air duct

Please design the air duct as below recommended picture

3.2.7 Change the air inlet direction

① Take off ventilation panel and flange, cut off the staples at side rail.

② Stick the attached seal sponge as per the indicating place in the following fig, and then change the mounting positions of air return panel and air return flange .

③ When install the filter mesh, please plug it into flange inclined from air return opening, and then push up.

④ The installation has finish, upon filter mesh which fixing blocks have been insert to the flange positional holes.

- A6 duct indoor unit installation

3.4.1 Service space for indoor unit

3.4.2 Bolt pitch

| Capacity(KBtu) | Size of outline dimension mounted plug |
| --- | --- |
|  | L | M |
| 24 | 1140 | 598 |

3.4.3 Hang indoor unit

1. Please refer to the upper data to locate the four positioning screw bolt hole on the ceiling. Be sure to mark the areas where ceiling hook holes will be drilled.

2. Install and fit pipes and wires after you have finished installing the main body. When choosing where to start, determine the direction of the pipes to be drawn out. Especially in cases where there is a ceiling

involved, align the refrigerant pipes, drain pipes, and indoor and outdoor lines with their connection points before mounting the unit.

3. Install hanging screw bolts.

- Cut off the roof beam.

- Strengthen the place that has been cut off, and consolidate the roof beam.

4. After you select an installation location, align the refrigerant pipes, drain pipes, as well as indoor and outdoor wires with their connection points before mounting the unit.

5. Drill 4 holes 10cm (4”) deep at the ceiling hook positions in the internal ceiling. Be sure to hold the drill at a 90° angle to the ceiling.

6. Secure the bolt using the washers and nuts provided.

7. Install the four suspension bolts.

8. Mount the indoor unit with at least two people to lift and secure it. Insert suspension bolts into the unit’s hanging holes. Fasten them using the washers and nuts provided.

9. Mount the indoor unit onto the hanging screw bolts with a block. Position the indoor unit flat using a level indicator to prevent leaks.

Note: Confirm the minimum drain tilt is 1/100 or more.

- Duct and accessories installation

1. Install the filter (optional) according to the size of the air inlet.

2. Install the canvas tie-in between the body and the duct.

3. Air inlet and air outlet duct should be apart far enough to avoid air passage short-circuit.

4. Connect the duct according to the following diagram.

5.Please refer to the following static pressure to install..

| Model(KBtu/h) | Static Pressure(Pa) |
| --- | --- |
| 24 | 0-100 |

Change the fan motor static pressure corresponding to external duct static pressure.

NOTE: 1.Do not put the connecting duct weight on the indoor unit.

2.When connecting duct, use inflammable canvas tie-in to prevent vibrating.

3. Insulation foam must be wrapped outside the duct to avoid condensate. An internal duct

underlayer can be added to reduce noise, if the end-user requires.

3.8.5 Adjust the air inlet direction(From rear side to under-side.)

① Take off ventilation panel and flange, cut off the staples at side rail

② Change the mounting positions of ventilation panel and air return flange .

③ When installing the filter mesh, fit it into the flange as illustrated in the following figure.

NOTE: All the figures in this manual are for explanation purpose only. They may be slightly different from the air conditioner you purchased.

- Air handler indoor unit installation

3.5.1 Service space for indoor unit

Refrigerant piping and connections- minimum12" recommended.

Maintenance and servicing access - minimum36" from front of unit recommended for blower motor/coil replacement.

Filter removal - minimum 36" recommended.

Plenum Clearances:

3.5.2 Install the main body

You can choose vertical or horizontal installation in accordance with the applications.

Note: For drain the condensate out of the unit smoothly, please place the unit with a small angle when horizontal installation.

3.5.3 Install the air duct

Typical air duct design:

Vertical Installation

Horizontal Installation

Outdoor unit installation (Top Discharge Unit)

- Location selection

Before starting the installation, select and check the suitability of the location for both the indoor and outdoor unit. Observe all limitations and clearance requirements. The outdoor unit must have sufficient clearance for air entrance to the condenser coil, for air discharge and for service access.

Note: For multiple unit installations, units must be spaced a minimum of 18 inches apart. (Coil face to coil face.)

If the unit is to be installed on a hot sun exposed roof or a black-topped ground area, the unit should be raised sufficiently above the roof or ground to avoid taking the accumulated layer of hot air into the outdoor unit.

Provide an adequate structural support.

- Service space for outdoor unit

- Install the Unit

On ground installation

The unit may be installed at ground level on a solid base that will not shift or settle, causing strain on the refrigerant lines and possible leaks. Maintain the clearances shown in Fig.5 and install the unit in a level position.

Normal operating sound levels may be objectionable if the unit is placed directly under windows of certain rooms (bedrooms, study, etc.).

Top of unit discharge area must be unrestricted for at least 6 feet above the unit.

Warning: The outdoor unit should not be installed in an area where mud or ice could cause personal injury.

Elevate the unit sufficiently to prevent any blockage of the air entrances by snow in areas where there will be snow accumulation. Check the local weather bureau for the expected snow accumulation in your area. Isolate the unit from rain gutters to avoid any possible wash out of the foundation.

On roof installation

When installing units on a roof, the structure must be capable of supporting the total weight of the unit, including a padded frame unit, rails, etc., which should be used to minimize the transmission of sound or vibration into the conditioned space.

Factory preferred tie-down method (Optional)

Note:

These instructions are intended as a method to tie-down system to cement slab as a securing procedure for high and areas. It is recommended to check Local codes for tie-down methods and protocols.

Step 1: Prior to installing clear pad of debris.

Step 2: Ensure cement pad is level.

IMPORTANT: Then cement pad must be made of HVAC-approved materials and must be the proper thickness to accommodate fasteners.

Step 3: Center unit onto pad.

Step 4: Fasten 4 L-shaped stainless steel braces onto cabinet base using 4 1/4” * 1/2” Hex washer head stainless steel self-tapping screws where indicated in following picture.

IMPORTANT: Do not use screws longer than indicated 1/4” * 2/3” and make sure that the brace is attached on center of base ban where indicated in Fig.7. Damage will occur to system.

Step 5: Drill 4 holes into cement base ensuring holes are 2  1//2”dp.

Step 6: Assemble unit to cement pad using 4 1/4” * 2” Hex washer head

cement screws  make sure not to over tighten.

Step 7:Finish unit assembly process as indicated in installation manual.

Refrigerant pipe installation

- Maximum pipe length and height drop

Considering the allowable pipe length and height drop to decide the installation position. Make sure the distance and height drop between indoor and outdoor unit not exceeded the date in the following table.

| Model | Max. Length | Max. Elevation |
| --- | --- | --- |
| 24,000 Btu/h | 25m | 15m |
| 30,000 Btu/h - 36,000 Btu/h | 30m | 20m |
| 42,000 Btu/h - 60,000 Btu/h | 50m | 30m |

- The procedure of connecting pipes

- Choose the pipe size according to the specification table.

- Confirm the cross way of the pipes.

- Measure the necessary pipe length.

- Cut the selected pipe with pipe cutter

- Make the section flat and smooth.

- Insulate the copper pipe

- Before test operation, the joint parts should not be heat insulated.

- Flare the pipe

- Insert a flare nut into the pipe before flaring the pipe

- According to the following table to flare the pipe

| Pipe diameter | Flare dimension A (mm) | Flare shape |
| --- | --- | --- |
|  | Min | Max |  |
| 1/4" (6.35) | 8.3 | 8.7 |  |
| 3/8" (9.52) | 12.0 | 12.4 |  |
| 1/2" (12.7) | 15.4 | 15.8 |  |
| 5/8" (15.9) | 18.6 | 19.1 |  |
| 3/4" (19) | 22.9 | 23.3 |  |

- After flared the pipe, the opening part must be seal by end cover or adhesive tape to avoid duct or exogenous impurity come into the pipe.

- Drill holes if the pipes need to pass the wall.

- According to the field condition to bend the pipes so that it can pass the wall smoothly.

- Bind and wrap the wire together with the insulated pipe if necessary.

- Set the wall conduit

- Set the supporter for the pipe.

- Locate the pipe and fix it by supporter

- For horizontal refrigerant pipe, the distance between supporters should not be exceed 1m.

- For vertical refrigerant pipe, the distance between supporters should not be exceed 1.5m.

- Connect the pipe to indoor unit and outdoor unit by using two spanners (Side discharge outdoor unit).

- Be sure to use two spanners and proper torque to fasten the nut, too large torque will damage the flare, and too small torque may cause leakage. Refer the following table for different pipe connection.

| Pipe Diameter | Torque | Sketch map |
| --- | --- | --- |
|  | (kgf.cm) | (N.cm) |  |
| 1/4" (6.35) | 144~176 | 1420~1720 |  |
| 3/8" (9.52) | 333~407 | 3270~3990 |  |
| 1/2" (12.7) | 504~616 | 4950~6030 |  |
| 5/8" (15.9) | 630~770 | 6180~7540 |  |
| 3/4" (19) | 990~1210 | 9270~11860 |  |

- Connect the pipe to indoor unit and outdoor unit by brazing (Top discharge outdoor unit and Air Handler indoor units)

- Top discharge outdoor unit and air handler indoor units connections are copper-to-copper and should be brazed with a phosphorous-copper alloy material such as Silfos-5 or equivalent. DO NOT use soft solder. The outdoor units have reusable service valves on both the liquid and vapor connections. The total system refrigerant charge is retained within the outdoor unit during shipping and installation. The reusable service valves are provided to evacuate and charge per this instruction.

- Serious service problems can be avoided by taking adequate precautions to assure an internally clean and dry system.

CAUTION: Dry nitrogen should always be supplied through the tubing while it is being brazed, because the temperature required is high enough to cause oxidation of the copper unless an inert atmosphere is provide. The flow of dry nitrogen should continue until the joint has cooled. Always use a pressure regulator and safety valve to insure that only low pressure dry nitrogen is introduced into the tubing. Only a small flow is necessary to displace air and prevent oxidation.

- Precautions should be taken to prevent heat damage to service valve by wrapping a wet rag around it as shown in following picture. Also, protect all painted surfaces, insulation, during brazing. After brazing cool joint with wet rag.

- Valve can be opened by removing the plunger cap and fully inserting a hex wrench into the stem and backing out counter-clockwise until valve stem just touches the chamfered retaining wall.

Drainage pipe installation

Install the drainage pipe as shown below and take measures against condensation. Improperly installation could lead to leakage and eventually wet furniture and belongings.

- Installation principle

- Ensure at least 1/100 slope of the drainage pipe

- Adopt suitable pipe diameter

- Adopt nearby condensate water discharge

- Key points of drainage water pipe installation

- Considering the pipeline route and elevation

- Before installing condensate water pipeline, determine its route and elevation to avoid intersection with other pipelines and ensure slope is straight.

- Drainage pipe selection

- The drainage pipe diameter shall not small than the drain hose of indoor unit

- According to the water flowrate and drainage pipe slope to choose the suitable pipe, the water flowrate is decided by the capacity of indoor unit.

Relationship between water flowrate and capacity of indoor unit

| Capacity (x1000Btu) | Water flowrate (l/h) |
| --- | --- |
| 12 | 2.4 |
| 18 | 4 |
| 24 | 6 |
| 30 | 7 |
| 36 | 8 |
| 42 | 10 |
| 48 | 12 |
| 60 | 14 |

According to the above table to calculate the total water flowrate for the confluence pipe selection.

For horizontal drainage pipe (The following table is for reference)

| PVC pipe | Reference value of inner diameter of pipe (mm) | Allowable maximum water flowrate (l/h) | Remark |
| --- | --- | --- | --- |
|  |  | Slope 1/50 | Slope 1/100 |  |
| PVC25 | 20 | 39 | 27 | For branch pipe |
| PVC32 | 25 | 70 | 50 |  |
| PVC40 | 31 | 125 | 88 | Could be used for confluence pipe |
| PVC50 | 40 | 247 | 175 |  |
| PVC63 | 51 | 473 | 334 |  |

Attention: Adopt PVC40 or bigger pipe to be the main pipe.

For Vertical drainage pipe (The following table is for reference)

| PVC pipe | Reference value of inner diameter of pipe (mm) | Allowable maximum water flowrate (l/h) | Remark |
| --- | --- | --- | --- |
| PVC25 | 20 | 220 | For branch pipe |
| PVC32 | 25 | 410 |  |
| PVC40 | 31 | 730 | Could be used for confluence pipe |
| PVC50 | 40 | 1440 |  |
| PVC63 | 51 | 2760 |  |
| PVC75 | 67 | 5710 |  |
| PVC90 | 77 | 8280 |  |

Attention: Adopt PVC40 or bigger pipe to be the main pipe.

- Individual design of drainage pipe system

- The drainage pipe of air conditioner shall be installed separately with other sewage pipe, rainwater pipe and drainage pipe in building.

- The drainage pipe of the indoor unit with water pump should be apart from the one without water pump.

- Supporter gap of drainage pipe

- In general, the supporter gap of the drainage pipe horizontal pipe and vertical pipe is respectively 1m~1.5m and 1.5m~2.0m.

- Each vertical pipe shall be equipped with not less than two hangers.

- Overlarge hanger gap for horizontal pipe shall create bending, thus leading to air block.

- The horizontal pipe layout should avoid converse flow or bad flow

- The correct installation will not cause converse water flow and the slope of the branch pipes can be adjusted freely

- The false installation will cause converse water flow and the slope of the branch pipe can not be adjusted.

- Water storage pipe setting

- If the indoor unit has high extra static pressure and without water pump to elevate the condensate water, such as high extra static pressure duct unit , the water storage pipe should be set to avoid converse flow or blow water phenomena.

- Lifting pipe setting of indoor unit with water pump

- The length of lifting pipe should not exceed the pump head of indoor unit water pump.

Pump head of big four way cassette: 750mm

Pump head of compact four way cassette: 500mm

- The drainage pipe should be set down inclined after the lifting pipe immediately to avoid wrong operation of water level switch.

- Refer the following picture for installation reference.

- Blowhole setting

- For the concentrated drainage pipe system, there should design a blowhole at the highest point of main pipe to ensure the condensate water discharge smoothly.

- The air outlet shall face down to prevent dirt entering pipe.

- Each indoor unit of the system should be installed it.

- The installation should be considering the convenience for future cleaning.

- The end of drainage pipe shall not contact with ground directly.

- Drainage test

- Water leakage test

After finishing the construction of drainage pipe system, fill the pipe with water and keep it for 24 hours to check whether there is leakage at joint section.

- Water discharge test

1.	Natural drainage mode(the indoor unit with outdoor drainage pump)

Infuse above 600ml water through water test hole slowly into the water collector, observe whether the water can discharge through the transparent hard pipe at drainage outlet.

2.	Pump drainage mode

2.1	Disconnect the plug of water level switch, remove the cover of water test hole and slowly infuse about 2000ml water through the water test hole, be sure that the water will not touch the motor of drainage pump.

2.2	Power on and let the air conditioner operate for cooling. Check operation status of drainage pump, and then connect the plug of water level switch, check the operation sound of water pump and observe whether the water can discharge through the transparent hard pipe at drainage outlet. (In light of the length of drainage pipe, water shall be discharged about 1 minute delayed)

2.3	Stop the operation of air conditioner, power off the power supply and put the cover of water test hole back to the original place.

a.	After stopped the air conditioner 3 minutes, check whether there is anything abnormal. If drainage pipes have not been distributed properly, over back-flow water shall cause the flashing of alarm indicator at remote-controlled receiving board and even water shall run over the water collector.

b.	Continuously infusing water until water level alarmed, check whether the drainage pump could discharge water at once. If water level does not decline under warning water level 3 minutes later, it shall cause shutdown of unit. When this situation happens, the normal startup only can be recovered by turning down power supply and eliminating accumulated water.

Note: Drain plug at the main water-containing plate is used for eliminating accumulated water in water-containing plate when maintaining air conditioner fault. During normal operation, the plug shall be filled in to prevent leakage.

- Insulation work of drainage pipe

Refer the introduction to the insulation engineering parts.

Vacuum Drying and Leakage Checking

- Purpose of vacuum drying

- Eliminating moisture in system to prevent the phenomena of ice-blockage and copper oxidation.

Ice-blockage shall cause abnormal operation of system, while copper oxide shall damage compressor.

- Eliminating the non-condensable gas (air) in system to prevent the components oxidizing, pressure fluctuation and bad heat exchange during the operation of system.

- Selection of vacuum pump

- The ultimate vacuum degree of vacuum pump shall be -756mmHg or above.

- Precision of vacuum pump shall reach 0.02mmHg or above.

- Operation procedure for vacuum drying

Due to different construction environment, two kinds of vacuum drying ways could be chosen, namely ordinary vacuum drying and special vacuum drying.

- Ordinary vacuum drying

1.  When conduct first vacuum drying, connect pressure gauge to the infusing mouth of gas pipe and liquid pipe, and keep vacuum pump running for 1hour (vacuum degree of vacuum pump shall be reached -755mmHg).

2   If the vacuum degree of vacuum pump could not reach -755mmHg after 1 hour of drying, it indicates that there is moisture or leakage in pipeline system and need to go on with drying for half an hour.

3   If the vacuum degree of vacuum pump still could not reach -755mmHg after 1.5 hours of drying, check whether there is leakage source.

4   Leakage test: After the vacuum degree reaches -755mmHg, stop vacuum drying and keep the pressure for 1 hour. If the indicator of vacuum gauge does not go up, it is qualified. If going up, it indicates that there is moisture or leak source.

- Special vacuum drying

The special vacuum drying method shall be adopted when:

1.   Finding moisture during flushing refrigerant pipe.

2.   Conducting construction on rainy day, because rain water might penetrated into pipeline.

3.   Construction period is long, and rain water might penetrated into pipeline.

4.   Rain water might penetrate into pipeline during construction.

Procedures of special vacuum drying are as follows:

1.   Vacuum drying for 1 hour.

2.   Vacuum damage, filling nitrogen to reach 0.5Kgf/cm2 .

Because nitrogen is dry gas, vacuum damage could achieve the effect of vacuum drying, but this method could not achieve drying thoroughly when there is too much moisture. Therefore, special attention shall be drawn to prevent the entering of water and the formation of condensate water.

3.   Vacuum drying again for half an hour.

If the pressure reached -755mmHg, start to pressure leakage test. If it can not reached the value, repeat vacuum damage and vacuum drying again for 1 hour.

4   Leakage test: After the vacuum degree reaches -755mmHg, stop vacuum drying and keep the pressure for 1 hour. If the indicator of vacuum gauge does not go up, it is qualified. If going up, it indicates that there is moisture or leak source.

Additional refrigerant charge

- After the vacuum drying process is carried out, the additional refrigerant charge process need to be performed.

- The outdoor unit is factory charged with refrigerant. The additional refrigerant charge volume is decided by the diameter and length of the liquid pipe between indoor and outdoor unit. Refer the following formula to calculate the charge volume.

| Diameter of liquid pipe (mm) | Φ6.35 | Φ9.52 |
| --- | --- | --- |
| Formula | V=15g×(L-5) | V=30g×(L-5) |

V: Additional refrigerant charge volume (g).

L : The length of the liquid pipe (m).

Note:

- Refrigerant may only be charged after performed the vacuum drying process.

- Always use gloves and glasses to protect your hands and eyes during the charge work.

- Use electronic scale or fluid infusion apparatus to weight refrigerant to be recharged. Be sure to avoid extra refrigerant charged, it may cause liquid hammer of the compressor or protections.

- Use supplementing flexible pipe to connect refrigerant cylinder, pressure gauge and outdoor unit. And The refrigerant should be charged in liquid state. Before recharging, The air in the flexible pipe and manifold gauge should be exhausted.

- After finished refrigerant recharge process, check whether there is refrigerant leakage at the connection joint part.(Using gas leakage detector or soap water to detect).

Engineering of insulation

- Insulation of refrigerant pipe

- Operational procedure of refrigerant pipe insulation

Cut the suitable pipe → insulation (except joint section) → flare the pipe → piping layout and connection→ vacuum drying → insulate the joint parts

- Purpose of refrigerant pipe insulation

- During operation, temperature of gas pipe and liquid pipe shall be over-heating or over-cooling extremely. Therefore, it is necessary to carry out insulation; otherwise it shall debase the performance of unit and burn compressor.

- Gas pipe temperature is very low during cooling. If insulation is not enough, it shall form dew and cause leakage.

- Temperature of gas pipe is very high (generally 50-100℃) during heating. Insulation work must be carried out to prevent hurt by carelessness touching.

- Insulation material selection for refrigerant pipe

- The burning performance should over 120℃

- According to the local law to choose insulation materials

- The thickness of insulation layer shall be above 10mm.If in hot or wet environment place, the layer of insulation should be thicker accordingly.

- Installation highlights of insulation construction

- Gas pipe and liquid pipe shall be insulated separately, if the gas pipe and liquid pipe were insulated together; it will decrease the performance of air conditioner.

- The insulation material at the joint pipe shall be 5~10cm longer than the gap of the insulation material.

- The insulation material at the joint pipe shall be inserted into the gap of the insulation material.

- The insulation material at the joint pipe shall be banded to the gap pipe and liquid pipe tightly.

- The linking part should be use glue to paste together

- Be sure not bind the insulation material over-tight, it may extrude out the air in the material to cause bad insulation and cause easy aging of the material.

- Insulation of drainage pipe

- Operational procedure of refrigerant pipe insulation

Select the suitable pipe → insulation (except joint section) → piping layout and connection→ drainage test→ insulate the joint parts

- Purpose of drainage pipe insulation

The temperature of condensate drainage water is very low. If insulation is not enough, it shall form dew and cause leakage to damage the house decoration.

- Insulation material selection for drainage pipe

- The insulation material should be flame retardant material, the flame retardant of the material should be selected according to the local law.

- Thickness of insulation layer is usually above 10mm.

- Use specific glue to paste the seam of insulation material, and then bind with adhesive tape. The width of tape shall not be less than 5cm. Make sure it is firm and avoid dew.

- Installation and highlights of insulation construction

- The single pipe should be insulated before connecting to another pipe, the joint part should be insulated after the drainage test.

- There should be no insulation gap between the insulation material.

Engineering of electrical wiring

- Highlights of electrical wiring installation

- All field wiring construction should be finished by qualified electrician.

- Air conditioning equipment should be grounded according to the local electrical regulations.

- Current leakage protection switch should be installed.

- Do not connect the power wire to the terminal of signal wire.

- When power wire is parallel with signal wire, put wires to their own wire tube and remain at least 300mm gap.

- According to table in indoor part named “the specification of the power” to choose the wiring, make sure the selected wiring not small than the date showing in the table.

- Select different colors for different wire according to relevant regulations.

- Do not use metal wire tube at the place with acid or alkali corrosion, adopt plastic wire tube to replace it.

- There must be not wire connect joint in the wire tube If joint is a must, set a connection box at the place.

- The wiring with different voltage should not be in one wire tube.

- Ensure that the color of the wires of outdoor and the terminal No. are same as those of indoor unit respectively.

Test operation

- The test operation must be carried out after the entire installation has been  completed.

- Please confirm the following points before the test operation.

- The indoor unit and outdoor unit are installed properly.

- Tubing and wiring are correctly completed.

- The refrigerant pipe system is leakage-checked.

- The drainage is unimpeded.

- The ground wiring is connected correctly.

- The length of the tubing and the added stow capacity of the refrigerant have been recorded.

- The power voltage fits the rated voltage of the air conditioner.

- There is no obstacle at the outlet and inlet of the outdoor and indoor units.

- The gas-side and liquid-side stop values are both opened.

- The air conditioner is pre-heated by turning on the power.

- Test operation

Set the air conditioner under the mode of "COOLING" by remote controller, and check the following points.

Indoor unit

- Whether the switch on the remote controller works well.

- Whether the buttons on the remote controller works well.

- Whether the air flow louver moves normally.

- Whether the room temperature is adjusted well.

- Whether the indicator lights normally.

- Whether the temporary buttons works well.

- Whether the drainage is normal.

- Whether there is vibration or abnormal noise during operation.

Outdoor unit

- Whether there is vibration or abnormal noise during operation.

- Whether the generated wind, noise, or condensed of by the air conditioner have influenced your neighborhood.

- Whether any of the refrigerant is leaked.

Part 5
Electrical Control System

1.	Electrical Control Function	106

2.	Troubleshooting	111

3.	Controller	130

Electrical Control Function

1.1 Definition

T1:  Indoor room temperature

T2:  Coil temperature of evaporator

T3:  Coil temperature of condenser

T4:  Outdoor ambient temperature

T5:  Compressor discharge temperature

1.2 Main Protection

1.2.1 Time delay at restart for compressor.

1.2.2 Temperature protection of compressor discharge

When the compressor discharge temp. is getting higher, the running frequency will be limited as below rules:

1.2.3 Sensor protection at open circuit and breaking disconnection.

1.2.4 Indoor fan delayed open function

When the unit starts up, the louver will be active immediately and the indoor fan will open 7s later.

If the unit runs in heating mode, the indoor fan will be also controlled by anti-cold wind function.

1.3 Operation Modes and Functions

1.3.1 Fan mode

(1) Outdoor fan and compressor stop.

(2) Temperature setting function is disabled, and no setting temperature is displayed.

(3) The louver operates same as in cooling mode.

(4) Auto fan:

1.3.2 Cooling Mode

1.3.2.1 Outdoor fan running rules

The outdoor unit will be run at different fan speed according to T4.

1.3.2.3 Indoor fan running rules

In cooling mode, indoor fan runs all the time and the speed can be selected as high, medium, low, auto and silent. When the compressor is running, the indoor fan is controlled as below:

The auto fan acts as below rules:

1.3.2.3 Evaporator low temperature T2 protection.

---T2<0℃, the compressor will stop and restart when T2≥5℃.

---0℃≤T2<4℃, the compressor frequency will be limited and decreased to the lower level until to stop the unit per minute

---4℃≤T2<7℃, the compressor will keep the current frequency.

---T2>7℃, the compressor frequency will not be limited.

1.3.2.4 Condenser high temperature T3 protection

.

1.3.3 Auto-mode

This mode can be chosen with remote controller and the setting temperature can be changed between 17~30℃.

In auto mode, the machine will choose cooling, heating or fan-only mode according to ΔT (ΔT =T1-Ts).

Heating*: For cooling only models, they will run at fan only.

Indoor fan will run at auto fan of the relevant mode.

The louver operates same as in relevant mode.

If the machine switches mode between heating and cooling, the compressor will keep stopping for 15 minutes and then choose mode according to T1-Ts.

If the setting temperature is modified, the machine will choose running function again.

1.3.4 Drying mode

Indoor fan speed is fixed at breeze and can’t be changed.

All protections are active and the same as that in cooling mode.

1.3.5 Timer function

1.3.5.1 Timing range is 24 hours.

1.3.5.2 Timer on. The machine will turn on automatically when reaching the setting time.

1.3.5.3 Timer off. The machine will turn off automatically when reaching the setting time.

1.3.5.4 Timer on/off. The machine will turn on automatically when reaching the setting “on” time, and then turn off automatically when reaching the setting “off” time.

1.3.5.5 Timer off/on. The machine will turn off automatically when reaching the setting “off” time, and then turn on automatically when reaching the setting “on” time.

1.3.5.6 The timer function will not change the AC current operation mode. Suppose AC is off now, it will not start up firstly after setting the “timer off” function. And when reaching the setting time, the timer LED will be off and the AC running mode has not been changed.

1.3.5.7 The setting time is relative time.

1.3.6 Economy function

1.3.6.1 The sleep function is available in cooling, heating or auto mode.

1.3.6.2. Operation process in sleep mode is as follow:

When cooling, the setting temperature rises 1℃ (be lower than 30℃) every one hour, 2 hours later the setting temperature stops rising and the indoor fan is fixed at low speed.

When heating, the setting temperature decreases 1℃ (be higher than 17℃) every one hour, 2 hours later the setting temperature stops rising and indoor fan is fixed at low speed. (Anti-cold wind function has the priority).

1.3.6.3 Operation time in sleep mode is 7 hours. After 7 hours the AC quits this mode but doesn’t turns off, but for console, the unit will turn off.

1.3.6.4 Timer setting is available

1.3.7 Auto-Restart function

The indoor unit is equipped with auto-restart function, which is carried out through an auto-restart module. In case of a sudden power failure, the module memorizes the setting conditions before the power failure. The unit will resume the previous operation setting (not including economy function and auxiliary functions) automatically after 3 minutes when power returns.

1.3.8 Drain pump control (For Cassette)

Adopt the water-level switch to control the action of drain pump.

Main action under different condition :( every 5 seconds the system will check the water level one time)

1. When the A/C operates with cooling (including auto cooling) and forced cooling mode, the pump will start running immediately and continuously, till stop cooling.

2. Once the water level increase and up to the control point, LED will alarm and the drain pump open and continue checking the water level. If the water level fall down and LED disalarmed (drain pump delay close 1 minute) and operate with the last mode. Otherwise the entire system stop operating ( including the pump) and LED remain alarming after 3 minutes.

1.3.9 Follow me(Optional)

- If the indoor PCB receives the signal which results from pressing the FOLLOW ME button on remote controller, the buzzer will emit a sound and this indicates the follow me function is initiated. But when the indoor PCB receives signal which sent from remote controller every 3 minutes, the buzzer will not respond. When the unit is running with follow-me function, the PCB will control the unit according to the temperature from follow-me signal, and the temperature collection function of room temperature sensor will be shielded.

- When the follow-me function is available, the PCB will not respond according to the setting temperature from follow-me signal every 3 minutes.

- The PCB will take action to the mode change information from remote controller signal, and the follow-me function will be turned off. (if the wired remote controller does not initiate follow me function).

- When the unit is running with follow-me function, if the PCB doesn’t receive any signal from remote controller for 7 minutes or pressing FOLLOW ME button again, the follow-me function will be turned off automatically, and the temperature collection function of room temperature sensor will be available, the PCB will control the unit according to the room temperature detected from its own room temperature sensor and setting temperature.

- When the indoor PCB receives the follow-me signal from wired remote controller, the control is the same as that from wireless remote controller, but buzzer will not respond. When the PCB receives turning-off follow-me signal from wired remote controller, the unit will quit follow-me function at once. The follow-me function controlled by wired remote controller prevails that by wireless remote controller.

Troubleshooting

2.1. Display board

2.1.1 Icon explanation on indoor display board(Ceiling & Floor)

2.1.2 Icon explanation on indoor display board (Super slim cassette).

2.1.3 Icon explanation on indoor display board (Duct)

2.1.4 Auto-lifting panel of 4 way cassette

2.2. Self-diagnosis

Indoor unit malfunction

During malfunction or protection, the indicators and digital LED displays as follow:

| Malfunction | Error Code | Timer Lamp | Operation Lamp (flashes) |
| --- | --- | --- | --- |
| Indoor EEPROM malfunction | E0 | X | 1 |
| Communication malfunction between indoor and outdoor units | E1 | X | 2 |
| Open or short circuit of T1 temperature sensor | E4 | X | 5 |
| Open or short circuit of T2 temperature sensor | E5 | X | 6 |
| Refrigerant leakage detection | EC | X | 7 |
| Water level alarm | EE | X | 8 |
| Overcurrent protection (For some units) | F0 | O | 1 |
| Open or short circuit of T4 temperature sensor | F1 | O | 2 |
| Open or short circuit of T3 temperature sensor | F2 | O | 3 |
| Open or short circuit of T5 temperature sensor | F3 | O | 4 |
| Outdoor EEPROM malfunction (For some units) | F4 | O | 5 |
| Communication error between auto-lifting panel and slim cassette (For slim cassette with auto-lifting panel) | F7 | O | 8 |
| Auto-lifting panel is faulty (For slim cassette with auto-lifting panel) | F8 | O | 9 |
| Auto-lifting panel is not closed (For slim cassette with auto-lifting panel) | F9 | O | 10 |
| Dual chips communication malfunction(for A6 duct &Air handle type) | FA | O | 11 |
| IPM module malfunction | P0 | ☆ | 1 |
| DC voltage too high or too low protection | P1 | ☆ | 2 |
| Too low ambient temperature protection | P3 | ☆ | 4 |
| Inverter compressor drive protection | P4 | ☆ | 5 |
| Compressor low pressure protection | P6 | ☆ | 7 |
| O (on) X(off) ☆(flash at 2Hz) |

2.3. Resolving Typical Malfunctions

2.3.1 EEPROM error diagnosis and solution(E0/F4)

| Error Code | E0/F4 |
| --- | --- |
| Malfunction decision conditions | Indoor or outdoor PCB main chip does not receive feedback from EEPROM chip. |
| Supposed causes | Installation mistake PCB faulty |

Trouble shooting:

EEPROM: An electrically erasable programmable read-only memory whose contents can be erased and reprogrammed using a pulsed voltage.

Note: The two photos above are only for reference, it’s may be not same totally with the ones on your side.

Outdoor PCB

Indoor PCB

2.3.2 Communication malfunction between indoor and outdoor units diagnosis and solution(E1)

| Error Code | E1 |
| --- | --- |
| Malfunction decision conditions | Indoor unit does not receive the feedback from outdoor unit during 100 seconds and this condition happens four times continuously. |
| Supposed causes | Wiring mistake Indoor or outdoor PCB faulty |

Trouble shooting:

2.3.3 Open circuit or short circuit of temperature sensor diagnosis and solution(E4/E5/F1/F2/F3)

| Error Code | E4/E5/F1/F2/F3 |
| --- | --- |
| Malfunction decision conditions | If the sampling voltage is lower than 0.06V or higher than 4.94V, the LED will display the failure. |
| Supposed causes | Wiring mistake Sensor faulty PCB faulty |

Trouble shooting:

2.3.4 Refrigerant Leakage Detection diagnosis and solution(EC)

| Error Code | EC |
| --- | --- |
| Malfunction decision conditions | Define the evaporator coil temp.T2 of the compressor just starts running as Tcool. In the beginning 5 minutes after the compressor starts up, if T2 ＜Tcool－2℃ does not keep continuous 4 seconds and this situation happens 3 times, the display area will show “EC” and AC will turn off. |
| Supposed causes | T2 sensor faulty Indoor PCB faulty System problems, such as leakage or blocking. |

Trouble shooting:

2.3.5 Water-level alarm malfunction diagnosis and solution

| Error Code | EE |
| --- | --- |
| Malfunction decision conditions | If the sampling voltage is not 5V, the LED will display the failure. |
| Supposed causes | Wiring mistake Water-level switch faulty Water pump faulty Indoor PCB faulty |

2.3.6 IPM malfunction or IGBT over-strong current protection diagnosis and solution(P0)

| Error Code | P0 |
| --- | --- |
| Malfunction decision conditions | When the voltage signal that IPM send to compressor drive chip is abnormal, the display LED will show “P0” and AC will turn off. |
| Supposed causes | Wiring mistake; IPM malfunction; Outdoor fan ass’y faulty Compressor malfunction; Outdoor PCB faulty |

Trouble shooting:

P-U

P-V

P-N

P-W

2.3.7 DC voltage too high or too low protection diagnosis and solution(P1)

| Error Code | P1 |
| --- | --- |
| Malfunction decision conditions | An abnormal voltage rise or drop is detected by checking the specified voltage detection circuit. |
| Supposed causes | Power supply problems. System leakage or block PCB faulty |

Trouble shooting:

Remark:

Measure the DC voltage between P and N port. The normal value should be around 310V.

2.3.8 Inverter compressor drive error diagnosis and solution(P4)

| Error Code | P4 |
| --- | --- |
| Malfunction decision conditions | An abnormal inverter compressor drive is detected by a special detection circuit, including communication signal detection, voltage detection, compressor rotation speed signal detection and so on. |
| Supposed causes | Wiring mistake; IPM malfunction; Outdoor fan ass’y faulty Compressor malfunction; Outdoor PCB faulty |

Trouble shooting:

# 2.3.9. Compressor low pressure protection diagnosis and solution(P6)

| Malfunction conditions | If the sampling voltage is not 5V, the LED displays a failure code. |
| --- | --- |
| Possible causes | Wiring mistake Faulty over load protector System blockages Faulty outdoor PCB |

2.3.10 Super-Slim Cassettes with an Up-Down Panel

2.3.10.1 Communication Errors between Indoor Unit and Up-Down Panel

F7

2.3.10.2 Up-down panel is defective

F8

  - Temperature sensor checking

Disconnect the temperature sensor from PCB, measure the resistance value with a tester.

Temperature Sensors.

Room temp.(T1) sensor,

Indoor coil temp.(T2) sensor,

Outdoor coil temp.(T3) sensor,

Outdoor ambient temp.(T4) sensor,

Compressor discharge temp.(T5) sensor.

Measure the resistance value of each winding by using the multi-meter.

Appendix 1 Temperature Sensor Resistance Value Table  (℃--K)

| ℃ | K Ohm | ℃ | K Ohm | ℃ | K Ohm | ℃ | K Ohm |
| --- | --- | --- | --- | --- | --- | --- | --- |
| -20 | 115.266 | 20 | 12.6431 | 60 | 2.35774 | 100 | 0.62973 |
| -19 | 108.146 | 21 | 12.0561 | 61 | 2.27249 | 101 | 0.61148 |
| -18 | 101.517 | 22 | 11.5000 | 62 | 2.19073 | 102 | 0.59386 |
| -17 | 96.3423 | 23 | 10.9731 | 63 | 2.11241 | 103 | 0.57683 |
| -16 | 89.5865 | 24 | 10.4736 | 64 | 2.03732 | 104 | 0.56038 |
| -15 | 84.2190 | 25 | 10.000 | 65 | 1.96532 | 105 | 0.54448 |
| -14 | 79.3110 | 26 | 9.55074 | 66 | 1.89627 | 106 | 0.52912 |
| -13 | 74.5360 | 27 | 9.12445 | 67 | 1.83003 | 107 | 0.51426 |
| -12 | 70.1698 | 28 | 8.71983 | 68 | 1.76647 | 108 | 0.49989 |
| -11 | 66.0898 | 29 | 8.33566 | 69 | 1.70547 | 109 | 0.48600 |
| -10 | 62.2756 | 30 | 7.97078 | 70 | 1.64691 | 110 | 0.47256 |
| -9 | 58.7079 | 31 | 7.62411 | 71 | 1.59068 | 111 | 0.45957 |
| -8 | 56.3694 | 32 | 7.29464 | 72 | 1.53668 | 112 | 0.44699 |
| -7 | 52.2438 | 33 | 6.98142 | 73 | 1.48481 | 113 | 0.43482 |
| -6 | 49.3161 | 34 | 6.68355 | 74 | 1.43498 | 114 | 0.42304 |
| -5 | 46.5725 | 35 | 6.40021 | 75 | 1.38703 | 115 | 0.41164 |
| -4 | 44.0000 | 36 | 6.13059 | 76 | 1.34105 | 116 | 0.40060 |
| -3 | 41.5878 | 37 | 5.87359 | 77 | 1.29078 | 117 | 0.38991 |
| -2 | 39.8239 | 38 | 5.62961 | 78 | 1.25423 | 118 | 0.37956 |
| -1 | 37.1988 | 39 | 5.39689 | 79 | 1.21330 | 119 | 0.36954 |
| 0 | 35.2024 | 40 | 5.17519 | 80 | 1.17393 | 120 | 0.35982 |
| 1 | 33.3269 | 41 | 4.96392 | 81 | 1.13604 | 121 | 0.35042 |
| 2 | 31.5635 | 42 | 4.76253 | 82 | 1.09958 | 122 | 0.3413 |
| 3 | 29.9058 | 43 | 4.57050 | 83 | 1.06448 | 123 | 0.33246 |
| 4 | 28.3459 | 44 | 4.38736 | 84 | 1.03069 | 124 | 0.32390 |
| 5 | 26.8778 | 45 | 4.21263 | 85 | 0.99815 | 125 | 0.31559 |
| 6 | 25.4954 | 46 | 4.04589 | 86 | 0.96681 | 126 | 0.30754 |
| 7 | 24.1932 | 47 | 3.88673 | 87 | 0.93662 | 127 | 0.29974 |
| 8 | 22.5662 | 48 | 3.73476 | 88 | 0.90753 | 128 | 0.29216 |
| 9 | 21.8094 | 49 | 3.58962 | 89 | 0.87950 | 129 | 0.28482 |
| 10 | 20.7184 | 50 | 3.45097 | 90 | 0.85248 | 130 | 0.27770 |
| 11 | 19.6891 | 51 | 3.31847 | 91 | 0.82643 | 131 | 0.27078 |
| 12 | 18.7177 | 52 | 3.19183 | 92 | 0.80132 | 132 | 0.26408 |
| 13 | 17.8005 | 53 | 3.07075 | 93 | 0.77709 | 133 | 0.25757 |
| 14 | 16.9341 | 54 | 2.95896 | 94 | 0.75373 | 134 | 0.25125 |
| 15 | 16.1156 | 55 | 2.84421 | 95 | 0.73119 | 135 | 0.24512 |
| 16 | 15.3418 | 56 | 2.73823 | 96 | 0.70944 | 136 | 0.23916 |
| 17 | 14.6181 | 57 | 2.63682 | 97 | 0.68844 | 137 | 0.23338 |
| 18 | 13.9180 | 58 | 2.53973 | 98 | 0.66818 | 138 | 0.22776 |
| 19 | 13.2631 | 59 | 2.44677 | 99 | 0.64862 | 139 | 0.22231 |

Appendix 2

| Unit: ℃---K Discharge temp. sensor table |
| --- |
| -20 | 542.7 | 20 | 68.66 | 60 | 13.59 | 100 | 3.702 |
| -19 | 511.9 | 21 | 65.62 | 61 | 13.11 | 101 | 3.595 |
| -18 | 483 | 22 | 62.73 | 62 | 12.65 | 102 | 3.492 |
| -17 | 455.9 | 23 | 59.98 | 63 | 12.21 | 103 | 3.392 |
| -16 | 430.5 | 24 | 57.37 | 64 | 11.79 | 104 | 3.296 |
| -15 | 406.7 | 25 | 54.89 | 65 | 11.38 | 105 | 3.203 |
| -14 | 384.3 | 26 | 52.53 | 66 | 10.99 | 106 | 3.113 |
| -13 | 363.3 | 27 | 50.28 | 67 | 10.61 | 107 | 3.025 |
| -12 | 343.6 | 28 | 48.14 | 68 | 10.25 | 108 | 2.941 |
| -11 | 325.1 | 29 | 46.11 | 69 | 9.902 | 109 | 2.86 |
| -10 | 307.7 | 30 | 44.17 | 70 | 9.569 | 110 | 2.781 |
| -9 | 291.3 | 31 | 42.33 | 71 | 9.248 | 111 | 2.704 |
| -8 | 275.9 | 32 | 40.57 | 72 | 8.94 | 112 | 2.63 |
| -7 | 261.4 | 33 | 38.89 | 73 | 8.643 | 113 | 2.559 |
| -6 | 247.8 | 34 | 37.3 | 74 | 8.358 | 114 | 2.489 |
| -5 | 234.9 | 35 | 35.78 | 75 | 8.084 | 115 | 2.422 |
| -4 | 222.8 | 36 | 34.32 | 76 | 7.82 | 116 | 2.357 |
| -3 | 211.4 | 37 | 32.94 | 77 | 7.566 | 117 | 2.294 |
| -2 | 200.7 | 38 | 31.62 | 78 | 7.321 | 118 | 2.233 |
| -1 | 190.5 | 39 | 30.36 | 79 | 7.086 | 119 | 2.174 |
| 0 | 180.9 | 40 | 29.15 | 80 | 6.859 | 120 | 2.117 |
| 1 | 171.9 | 41 | 28 | 81 | 6.641 | 121 | 2.061 |
| 2 | 163.3 | 42 | 26.9 | 82 | 6.43 | 122 | 2.007 |
| 3 | 155.2 | 43 | 25.86 | 83 | 6.228 | 123 | 1.955 |
| 4 | 147.6 | 44 | 24.85 | 84 | 6.033 | 124 | 1.905 |
| 5 | 140.4 | 45 | 23.89 | 85 | 5.844 | 125 | 1.856 |
| 6 | 133.5 | 46 | 22.89 | 86 | 5.663 | 126 | 1.808 |
| 7 | 127.1 | 47 | 22.1 | 87 | 5.488 | 127 | 1.762 |
| 8 | 121 | 48 | 21.26 | 88 | 5.32 | 128 | 1.717 |
| 9 | 115.2 | 49 | 20.46 | 89 | 5.157 | 129 | 1.674 |
| 10 | 109.8 | 50 | 19.69 | 90 | 5 | 130 | 1.632 |
| 11 | 104.6 | 51 | 18.96 | 91 | 4.849 |  |  |
| 12 | 99.69 | 52 | 18.26 | 92 | 4.703 |  |  |
| 13 | 95.05 | 53 | 17.58 | 93 | 4.562 |  |  |
| 14 | 90.66 | 54 | 16.94 | 94 | 4.426 |  |  |
| 15 | 86.49 | 55 | 16.32 | 95 | 4.294 | B(25/50)=3950K |
| 16 | 82.54 | 56 | 15.73 | 96 | 4.167 |  |  |
| 17 | 78.79 | 57 | 15.16 | 97 | 4.045 | R(90℃)=5KΩ±3% |
| 18 | 75.24 | 58 | 14.62 | 98 | 3.927 |  |  |
| 19 | 71.86 | 59 | 14.09 | 99 | 3.812 |  |  |

Appendix 3

| Normal voltage of P and N |
| --- |
| 208-240V(1-phase,3-phase) | 380-420V(3-phase) |
| In standby |
| around 310VDC | around 530VDC |
| In operation |
| With passive PFC module | With partial active PFC module | With fully active PFC module | / |
| >200VDC | >310VDC | >370VDC | >450VDC |

Controller

3.1 Wireless Remote Controller

RG51Q1/BGE

The R51Q1/BGE wireless remote controller is standard for Four-way cassette type and the Ceiling& floor type.

General Function for wireless remote controller:

| Model | RG51Q1/BGE |
| --- | --- |
| Rated voltage | 3.0V(2pieces of LR03 7＃ batteries) |
| Min voltage for sending signal of CPU | 2.4V |
| Effective receiving distance | 8m~11m |
| Operation condition | -5~60℃ |

Buttons and functions:

1. Adjust: Increase the set temp. Keeping pressing will increase the temp with 1℃ per 0.5s.

2. Adjust : Reduce the set temp. Keeping pressing will reduce the temp. with 1℃ per 0.5s.

3. MODE: Once pressing, running mode will be selected in the following sequence:

AUTO	COOL   DRY    HEAT  FAN

NOTE: No heating mode for cool only type unit.

4. SWING: Activate or turn off horizontal swing function. (Only available when remote controller is used with corresponding unit, i.e. Ceiling & floor type)

5. SWING : Activate or turn off vertical swing function.

(Only available when remote controller is used with corresponding unit.)

AIR DIRECTION: Activate swing function of air deflector. Once pressing, air deflector will turn 6°. For normal operation and better cooling and heating effect, deflector will not turn to the degree which is the state of deflector when the unit is turned off.( Only available when remote controller is used with corresponding unit.)

6. RESET (inner located): Press this button with a needle of 1mm to cancel the current setting and reset remote controller.

7. ON/OFF: For turning on or turning off the air conditioner.

8. FAN SPEED: Fan speed will be selected in following sequence once pressing this button:

AUTO LOW   MED	 HIGH

9. TIME ON: For time ON setting. Once pressing this button, the time will increase by 0.5 hour. When the set time exceeds 10 hours, pressing the button will increase the time by 1 hour. Adjusting the figure to 0.00 will cancel time ON setting.

10. ECO: Activate or turn off economic operation mode. It is suggested to turn on this function when sleeping. (Only available when remote controller is used with corresponding unit.)

11. TIME OFF: For time OFF setting. Once pressing this button, the time will increase by 0.5 hour. When the set time exceeds 10 hours, pressing the button will increase the time by 1 hour.

12. C/H (inner located): Press this button with a needle of 1mm to shift mode between COOL only and COOL&HEAT. During setting, background light will be lightened. Factory default mode is COOL &HEAT.

3.2 Wired Remote Controller(Optional)

3.2.1 KJR-12B

Name and functions of buttons on the wire controller 1.	Mode button: When press this button, the operation mode change as the following sequence:

Remark: For the cooling only model, the heating mode is skipped.

2.	Timer on button: Press this button, timer on function is active. Then every press, the time increase 0.5h, after 10h, 1h increment after each press. If cancel this Function, just set it to "0.0"

3.	Timer off button: Press this button, timer off function is active. Then every press, the time increase 0.5h, after 10h, 1h increment after each press. If cancel this function, just set it to "0.0" .

4.	Follow me button: When under cool, heat and auto mode, press this button, follow me function is active. Press again, this function is ineffective.

5.	Electrical heater button: If press this button in heat mode, electrical heater function become ineffective.

6.	Reset button (hidden): Use a 1mm stick to press in the little hole , then the current setting is canceled . The wire controllers enter into original state.

7.	ON/OFF button: When in off state, press this button, the indicator is on, the wire controller enter into on state, and send setting information to indoor PCB. When in on state, press this button, the indicator is off, and send instruction. If timer on or timer off has been set, it cancel this setting then send instruction to stop the machine.

8.	Adjust button: Set indoor temperature up. If press and hold on, it will increase at 1degree per 0.5 second.

9.	Adjust button: Set indoor temperature down. if press and hold on, it will decrease at 1degree per 0.5 Second.

10.	Swing button: First press, start swing function; second press, stop swing. (Match to some model with swing function).

11.	Economy operation button: press this button, the indoor unit operates in economy mode, press again, exit this mode (it may be ineffective for some models)

12.	Fan speed button: press this button consecutively; the fan speed will circle as follow:

13.	Lock button (hidden): When you push the LOCK button, all current settings are locked in and the wire controller does not accept any operation except that of the LOCK button. Use the lock mode when you want to prevent setting from being changed accidentally or play fully. Push the LOCK button again when you want to cancel the LOCK mode.

Name and function of LCD on the wire controller

1.	Operation mode indication: When press” MODE” button, the following mode can be selected in circle. Auto Cool Dry Heat Fan only Auto.

Auto→ Cool→ Dry →Heat→ Fan only →Auto

For cooling only model, heat mode is skipped.

2.	Timer: When adjust setting on time or only on time is set, the “ON” is lighted. When adjust setting off time or only off time is set, the” OFF" is lighted. If on and off timer are both set, the “ON” and “OFF” are both lighted.

3.	Follow me function: There is a temperature sensor inside the wire controller, after setting temperature, it will compare the two temperatures, and the space of wire controller will be the same as setting temperature. It is available under cooling, heating, auto mode.

4	ON/OFF indication: When it is on, the icon display, otherwise it is extinguished.

5.	Fan speed indication: There are four fan modes: low, middle, high, auto. For some models, no middle fan then the middle fan is seen as high speed.

6.	Lock: When the "LOCK" button is pressed, the icon appears and other buttons is unable, press again, the icon disappears.

7.	Temperature display zone: Generally it displays setting temperature; it can be adjusted by press temperature button▲and▼ .But in fan mode, no display here.

Remark:

The wired controller will reset to factory setting with auto mode, auto fan and 24℃ setting temperature when the air conditioner restarts after power failure.

And this may cause inconsistent displays on the wired controller and on the air conditioner. You need to readjust the running status through the wired controller.

Installation

Installation Notice:

When the air conditioner needs the constant frequency wire controller, be sure adding a wire joint with 5 terminal named A, B, C, D, E in indoor unit, and fixing an infrared emitter whose anode and cathode connecting with A and B near the receiver in the indoor unit switch board, then connecting the terminal +5v, GND, Run in the switch board to C,D,E respectively.

NOTE

●The connecting wire should be a little longer as to take away the switch board easily for maintenance.

●The connecting wire should be a little longer as to take away the controller easily for maintenance.

3.2.2 KJR-25B (Optional for Air Handler Indoor Unit)

Appearance

NAME AND FUNCTION OF THE WIRE CONTROLLER

FEATURES

Structure of thermostat and explanation for the keypads

YOUR THERMOSTAT REPLACES

| Description | KJR-25B |
| --- | --- |
| Heat Pump (No Aux. or Emergency Heat) | Yes |
| Heat Pump (with Aux. or Emergency Heat) | Yes |
| Standard Heat & Cooling Systems | Yes |
| Two Stage Heat & Two Stage Cool | Yes |
| Standard Heat Only Systems | Yes |
| Millivolt Heat Only Systems– Floor or Wall Furnaces | Yes |
| Standard Central Air Conditioning | Yes |
| Gas or Oil Heat | Yes |
| Electric Furnace | Yes |
| Hydronic (Hot Water) Zone Heat-2 Wires | Yes |
| Hydronic (Hot Water) Zone Heat–3 Wires | No |

This Thermostat will NOT control 110/220Volt systems.

IMPORTANT

2, Read the entire installation section of this Owner’s Manual thoroughly before you begin to install or operate your Thermostat.

This thermostat can be used for conventional or heat pump system, Please configure the thermostat according to Configuration Menu before operation.

REMOVE THE MYLAR LABEL FORM THE LCD DISPLAY WINDOW.

INSTALLATION

3,  All installation is normally performed at your thermostat.

COMPRESSOR PROTECTION

4，The thermostat provides a 4 minutes delay after shutting of the heating or cooling system before it can be restarted. This feature will prevent damage to your compressor caused by rapid cycling. Note that this delay also applies to the heating system control. It does not provide a delay when there are power outages.you can select the function on or off at the configuration.

TEMPERATURE RANGE

5,This thermostat can be programmed between 45°F and 95°F (7°C and 35°C). However, it will display room temperatures from 30°F to 99°F (0°C and 37°C). “HI” will be displayed if the temperature is higher than 99°F (37°C), and “LO” will be displayed if the temperature is lower than 30°F (0°C).This thermostat will automatically cutoff in Heat mode if the temperature rises above 95°F (35°C), and automatically cutoff in Cool mode if the temperature drops below 45°F (7°C). NOTE: if the thermostat measure a temperature over 99°F(37℃), ”HI” will be displayed on the LCD. if the temperature is below 32°F(0℃). and ”LO” will be displayed on the LCD.

POWER FAILURE

6， Whenever the main power is interrupted or fails, the battery power retains and current time. This thermostat has permanent memory, although you will have to reset your clock when there are power outages.

POWER SUPPLY

7，The thermostat shall be powered by 24 VAC and with batteries as backup.

BATTERY WARNING

8，Fresh alkaline batteries should provide about one year of service. However, when the batteries become drained, “BATT” will alternate on the display with the current time. When this message occurs, install 2 new AA batteries, You have approximately 1 minute to change the batteries and keep thermostat’s clock. Once the batteries have become too low to ensure proper operation, your system will be turned off, and the display will be cleared except for “BATT” flashing on the LCD display.

CAUTION: Once only the “BATT” only display occurs, the thermostat is shut down, and your system will no longer operate. In this condition, there is no temperature control of your dwelling. NOTE: The backlight will not function when the thermostat is in low battery condition.

NOTE: If you plan to be away from the premises over 30 days, we recommend that you replace the old batteries with new alkaline batteries prior to leaving

TYPICAL WIRING DIAGRAM

1 Typical wiring diagram for single transformer heat pump systems

2 Typical wiring diagram for two transformer heat pump systems with NO safety circuit

3 Typical wiring diagram for two transformer heat pump systems with safety circuits in BOTH systems

4 Typical wiring diagram for single transformer multi-stage systems

CHECK THERMOSTAT OPERATION

Note: To prevent static discharge problems, touch side of thermostat to release static build-up before touching any keys. If at any time during testing your system does not operate properly, contact a qualified serviceperson.

Fan Operation

If your system does not have a G terminal connection, skip to Heating System.

1. Turn on power to system.

2. Move FAN switch to ON position. The blower should begin to operate.

3. Move FAN switch to AUTO position. The blower should stop immediately.

Heating System

1. Move system switch to heat mode. If the auxiliary heating system has a standing pilot, be sure to light it.

2. Press to adjust thermostat setting to 1℃ above room temperature. The heating system should begin to operate. The display should show “STG1”. However, if the setpoint temperature display is flashing, the compressor lockout feature is operating (see Configuration menu, item 5).

3. Adjust temperature setting to 3° above room temperature. If your system configuration is set at MS2, HP2 or HP1, the auxiliary heat system should begin to operate and the display should show “STG1+2”.

4. Press to adjust the thermostat below room temperature. The heating system should stop operating.

Emergency System

EMER bypasses the Heat Pump to use the heat source wired to terminal E on the thermostat. EMER is typically used when compressor operation is not desired, or you prefer back-up heat only.

1. Press SYSTEM switch to select Heat mode. then press EMER key. “EMER” will show on the display.

2. Press to adjust thermostat setting above room temperature. The Aux. heating system will begin to operate. The display will show “STG1” “EMER”to indicate that the Aux. system is operating.

3. Adjust temperature setting to 2°C above room temperature. The auxiliary heat system should begin to operate and the display should show “STG1+2”.

4. Press to adjust the thermostat below room temperature. The Aux. heating system should stop operating.

Cooling System

1. Move SYSTEM switch to select the Cool mode.

2. Press to adjust thermostat setting below room temperature. The blower should come on immediately on high speed, followed by cold air circulation. The display should show “STG1”.

3. Adjust temperature setting to 2°C below room temperature. The second stage cooling should begin to operate and the display should show “STG1+2”

4. Press to adjust the temperature setting above room temperature. The cooling system should stop operating.

CONFIGURATION MENU

The step to enter the configuration menu:

1. Set SYSTEM switch to OFF,

2. Press both up and down keys  for 5 seconds to enter configuration menu. The display will show the first item in the configuration menu.

| INSTALLER/CONFIGURATION MENU |
| --- |
| Step | Press Button | Displayed | Press up or down key to select | Comments |
|  |  | (Factory Default) |  |  |
| 1 | Backlight button | MS2 | SS1 | Single stae |
|  |  |  | MS2 | Multi-stage |
|  |  |  | HP1 | Heat pump (single stage) |
|  |  |  | HP2 | Heat pump (2 stages) |
| 2 | Backlight button | (RECO)off | On | Recovery enable |
|  |  |  | Off | Recovery disabled |
| 3 | Backlight button | (SPAN)2 | 1 | Span(one stage)1 |
|  |  |  | 2 | Span(one stage)2 |
|  |  |  | 3 | Span(one stage)3 |
| 4 | Backlight button | (BLIT)on | On | Backlight on |
|  |  |  | Off | Backlight off |
| 5 | Backlight button | (SP2)2 | 1 | Span(one stage)1 |
|  |  |  | 2 | Span(one stage)2 |
|  |  |  | 3 | Span(one stage)3 |
| 6 | Backlight button | (TEMP)F | F | Selects temperature display °F |
|  |  |  | C | Selects temperature display °C |
| 7 | Backlight button | HOUR(12) | 12 | Selects time format display 12hours |
|  |  |  | 24 | Selects time format display 24hours |
| 8 | Backlight button | COMP(OFF) | Off | Selects Compressor Lockout OFF |
|  |  |  | On | Selects Compressor Lockout ON |
| 9 | Backlight button | COOL(2) | 2 | This model must select 2 |
|  |  |  | 1 | Just use for one stage system |
| 10 | Backlight button | FACT(0) | 0 | Display normal |
|  |  |  | 1 | Use for another model to go back to factory default |
|  |  |  | 2 | All the setting will go back to factory default |

The configuration menu allows you to set certain thermostat operating characteristics to your system or personal requirements.

The configuration menu table summarizes the configuration options. An explanation of each option follows. Press ”Backlight button”   to change to the next menu item. To exit the menu and return to the normal operation, press  key. If no keys are pressed within fifteen Seconds, the thermostat will revert to normal operation.

- Single Stage, Multi-stage or Heat Pump System Configuration

This control can be configured for Heat Pump or two stage heat/one stage cool multi-stage operation. The display indicates “MS2” (default for multi-stage mode) in the display. The Multi-stage configuration can be toggled to “SS1”, or “HP1” by pressing the up or down key. In Multi-stage configuration, EMER mode is useless.

- Fast or Slow Crycle Selection(one stage)

- Select Backlight function OFF or ON

- Fast or Slow Crycle Selection(two stage)

- Select F° or C° Readout.

Changes the display readout to Centigrade or Fahrenheit as required

- Selects time format display 12hours or 24hours

- Select Compressor Lockout COMP OFF or ON Selecting COMP ON will cause the thermostat to wait 4 minutes before turning on the compressor if the heating and cooling system loses power. It will also wait 5 minutes minimum between cooling and heating cycles. This is intended to help protect the compressor from short cycling. Some newer compressors already have a time delay built in and do not require this feature. Your compressor manufacturer can tell you if the lockout feature is already present in their system. When the thermostat compressor time delay occurs it will flash the setpoint for about four minutes.

- This model must select 1

- This model must select 1 to back factory Default

Setting Day and Time

■ The LCD will show this information when batteries are first installed. The temperature will update after a few seconds.

■ During time and day setting mode, the temperature displays will go blank.

Reviewing the Current Temperature Setting

Current time and temperature.

■ Press less than 1 second .

■ Set Temperature is shown above current room temperature.

OPERATION

System Selector Switch

The System Selector Switch on the front of the thermostat determines the Operating mode of the thermostat. You may select COOL , OFF , HEAT, In order to take full advantage of this thermostat’s feature.

NOTE: Anytime you install or remove the thermostat form the wallplate, slide the System Selector to the OFF position to prevent the possibility of a rapid system On-Off.

Fan Switch

The Fan switch should normally be located in the AUTO position. The Fan will be turned on along with normal operation of your system. In a normal gas or oil furnace, the Fan will be turned on by your furnace after its warm-up delay. For electric heat, air conditioning, and heat pump operation, the Fan will turn on with the system. To run the Fan on continuously, slide the Fan switch to the ON position.

Energy Monitor

■ The Energy monitor feature measures and stores the amount of time the heating and air conditioning

system operates. Usage can be display for Today (since 12 am), Yesterday, This Week (since Monday), Last Week (last Monday through Sunday), and Total (up to 999 Hrs). By monitoring your energy usage, you see how much the set-back periods are saving. To review energy usage, press to cycle through Today, Yesterday, this Week, Last Week, and Total. Press again to return to normal mode, or wait 15 seconds for the display to return to normal mode .You can also return to normal mode at any time by pressing RUN.

■ For example: This LCD display shows Today’s usage to be 10 Hours, 26 minutes.

■ Press and hold for 3 seconds to reset the Energy Monitor’s counters.

The display will blink, and counters will be cleared to zero.

NOTE: Clearing the Energy Monitor counter will also clear the Filter Monitor counter , as Filter usage and Total Energy usage are the same. Also, clearing the filter Monitor counter will clear ALL Energy Monitor counters as well.

Filter Monitor

Your thermostat also keeps a record of the number of hours your filter has been in use. To maximize your system’s performance and energy efficiency, change or clear your filter regularly.

■ When the total system run time for heat and cool reaches 500 hours, you need clean or change your system’s filter, “FILT” will continue to flash until the counter is set back to zero.

■ Press to review total filter usage. The display will blink “FILT”.Then show the filter Monitor counter. After

15seconds, the display will return to normal mode, or you can hit RUN to exit immediately.

The Filter Monitor will display up to 999 hours and 59 minutes of usage. In this example, the counter is at 410 Hours, 26 minutes.

■ To reset the Filter Monitor counter, depress FILTER for 3 seconds. The display will blink, and the counter will be reset to zero.

NOTE: Clearing the Filter Monitor counter will also clear ALL Energy Monitor counters, as Filter usage and Total Energy usage are the same. Also, clearing the Energy Monitor counters will clear the Filter Monitor counter as well.

Keyboard lock

The keyboard can be locked to prevent unauthorized changes to the thermostat.

To lock or unlock the keyboard, press and hold run Key for 3 seconds. The keyboard is locked. when LOCK appears on the display.

■ All keys are locked, Any time a key is pressed, LOCK will appear on the display for 1 second.

Backlighting

Your thermostat has an electroluminescent lamp that backlights the display for easy viewing in the dark.

When any key is pressed the display is illuminated.

The display will remain illuminated for 8 seconds after the last key is pressed.

This allows the light to stay on if you need to operate several keys.

NOTE: If the thermostat is in Low Battery warning condition, the backlight will not operate. Replace with 2 new AA alkaline batteries to restore the Backlight function.

Low Battery Warning

Your thermostat has a two-stage lower battery warning system. When the batteries are first detected to be weak, the first stage low battery warning is indicated by “BATT” flashing on the LCD display. At your earliest convenience, you need to replace the batteries with 2 new AA alkaline batteries.

When the batteries become too weak for normal operation, the thermostat enters the second stage low battery warning which shuts down the thermostat. In this condition, “BATT” flashes alone on the display, and the thermostat will turn your system Off. Your system will remain shut-off until the batteries are replaced.

NOTE: The thermostat will still keep the current Set Temperature and Filter run time in memory until new batteries are installed. After confirming that new batteries have been inserted, the thermostat will return to normal operation.

Error Mode

If the thermostat is unable to control your system due to an unexpected battery problem, the thermostat will enter Error Mode. In this condition, the thermostat flashes “E1”,“E2”,”E3”or”E4”on the LCD display, and shuts off your system. To correct this problem, replace the batteries with 2 new AA alkaline batteries, even if you have recently replaced them. Move the battery out, and then hold any key to release the rest energy. Then place the battery again. You will need confirm normal operation.

If Error Mode returns, please call us for further information.

| LCD display | Information |
| --- | --- |
| E1 | Sensor Error |
| E2 | System switch Error |
| E3 | No use |
| E4 | E2 memory Error |

Warning Mode

If the SYSTEM MONITOR SWITCH is close show the system have wrong. the thermostat flashs “E5”on the LCD display.

Auto Cut Off

Your thermostat will automatically cutoff in Heat mode if the room temperature rises above 95°F (35°C). It will cutoff in Cool mode if the room temperature drops below 40°F (4°C). Note that if your system has malfunctioned and no longer responds to thermostat controls, the Auto Cut-Off will have no effect.

TROUBLESHOOTING

| Problem | Solution |
| --- | --- |
| SCRAMBLED OR DOUBLE DISPLAY (numbers over numbers) | 1. Remove clear mylar sticker. |
| NO DISPLAY | 1. Check battery connections and batteries 2. Move the battery out, and then hold any key to release the rest energy. Then place the battery again. |
| ENTIRE DISPLAY DIMS | 1. Replace Batteries |
| AUTO/FAN DOES NOT TURN ON | 1. Move Elec/Gas selector to opposite position is in the correct position. 2. There may be as much as 4 minute delay before the Heat or Cool system turns On-wait and check. (Compressor protection delay). 3，Check your circuit breaks and switches to ensure there is power to the system. 4. Replace batteries. 5. Make sure your furnace blower door is closed properly. 6. Check the position of the Furnace or Heat Pump selector switches: Normal/O/B. |
| ERRATIC DISPLAY | 1. Move the battery out, and then hold any key to release the rest energy. Then place the battery again. |
| IF UNIT CONTINUES TO OPERATE IN THE OFF POSITION | 1. Replace unit |
| THERMOSTAT PERMANENTLY READS “E1”,”E2”,”E3”, “E4”. | 1. Replace unit |